## Cover
Infrastructure & Cities
Building Technologies Division
Title | X-FBs and assigned BA Objects
Subject | Specification
Project | <none>
Abstract | Brief summary of this document. |  |  |  | manual update
Keywords
Related Product(s)
Document Storage | ProjectShare
Dokument Category | ProjectRecord
Document Nummer
Revision | 2
Revision Date | 07-Apr-2014
Document Status | Final - valid without Approval
Author | Michael Speckien, 5556
Department | IC BT CPS R&D ZG CS SAP
Co-Author(s)
Responsible | Michael.Speckien@siemens.com
Company | Siemens Schweiz AG, Building Technologies Division
OrgUnit | Control Products & Systems
Classification | Restricted
Based on Template | Standard;16;2011-09-30;dh3531
Revision History | Rev | Date | Author | Remarks, Changes
| 2 | 07-Apr-2014 | Michael Speckien, 5556 | Status=Final - valid without Approval Objecttypes and rule for Object-ID added
| 1 | 28-Mrz-2014 | Michael Speckien, 5556 | Status=Final - valid without Approval
Template History | Rev | Date | Author | Remarks, Changes

## Tabelle1
Rule1: | If one of the X-FBs is of the type …., then the BA-Object is definitely of type …. -> Add one object.
Rule2: | If none of the X-FBs appies to rule 1, and one of the X-FBs is of type …, then the BA-Object is of default type … -> Show a warning, and add default object
Rule3: | If none of the X-FBs apply to rule1 or rule2, then the BA Object cannot be defined. -> Show an error, do not add an object
Rule4 | -> Ignore them (no warning, no error)
01 XFB | These rules apply for case 1&2:
Category |  | Datatype | Name | Compatible BACnet Objects
|  |  |  | ACalcVal | ACnfVal | AI | AO | APrcVal | BCalcVal | BcnfVal | BI | BO | BlsIn | BlsOut | BPrcVal | LgtAOut | LgtBOut | LgtIn | MCalcVal | MCnfVal | MI | MO | MPrcVal | UCnfVal
|  |  |  | ObjType = 2 | 2 | 0 | 1 | 2 | 5 | 5 | 3 | 4 | 259 | 258 | 5 | 260 | 261 | 262 | 19 | 19 | 13 | 14 | 19 | 48
Read | Single | Real | R_A | x | x | x | x | x
|  | Boolean | R_B | [5 empty] | x | x | x | x |  |  | x
|  | Unsigned | R_M | [15 empty] | x | x | x | x | x
|  | Unsigned | R_UNSG | [20 empty] | x
|  | Structure | R_LGTCMD | [12 empty] | x | x
|  | Structure | R_BLSCMD | [10 empty] | x
| Multiple | Real | R_AX | x | x | x | x | x
|  | Boolean | R_BX | [5 empty] | x | x | x | x |  |  | x
|  | Unsigned | R_MX | [15 empty] | x | x | x | x | x
|  | Structure | R_LGTX | [14 empty] | x
|  | Structure | R_BLSX | [9 empty] | x
Write | Single | Real | W_A | x
|  | Boolean | W_B | [5 empty] | x
|  | Unsigned | W_M | [15 empty] | x
Command | Single | Real | CMD_A |  |  |  | x | x
|  | Boolean | CMD_B | [8 empty] | x |  |  | x
|  | Unsigned | CMD_M | [18 empty] | x | x
|  | Structure | CMD_LGT | [12 empty] | x | x
|  | Structure | CMD_BLS | [10 empty] | x
| Multiple | Real | CMD_AX |  |  |  | x | x
|  | Boolean | CMD_BX | [8 empty] | x |  |  | x
|  | Unsigned | CMD_MX | [18 empty] | x | x
Read Property | Single | Real | RP_REAL | Allows access to any BACnet object property of datatype Real.
|  | Boolean | RP_BOOL | Allows access to any BACnet object property of datatype Boolean or BACnetBinaryPV.
|  | Unsigned | RP_UNSG | Allows access to any BACnet object property of datatype Unsigned (includes Multistate, Enumerated, and non-negative Integer*).
Write Property | Single | Real | WP_REAL | Allows access to any writable BACnet object property of datatype Real.
|  | Boolean | WP_BOOL | Allows access to any writable BACnet object property of datatype of Boolean or BACnetBinaryPV.
|  | Unsigned | WP_UNSG | Allows access to any writable BACnet object property of datatype Unsigned (includes Multistate, Enumerated, and non-negative Integer*).
Collecting | Group | Structure | R_AG | Allows access to any BACnet object property of datatype Real.
|  | Structure | R_BG | Allows access to any writable BACnet object property of datatype of Boolean or BACnetBinaryPV.
|  | Structure | R_MG | Allows access to any BACnet object property of datatype Unsigned (includes Multistate, Enumerated, and non-negative Integer*).
Distributing | Group | Structure | CMD_AG | Allows access to any BACnet object property of datatype Real.
|  | Structure | CMD_BG | Allows access to any writable BACnet object property of datatype of Boolean or BACnetBinaryPV.
|  | Structure | CMD_MG | Allows access to any BACnet object property of datatype Unsigned (includes Multistate, Enumerated, and non-negative Integer*).
|  | Structure | CMD_LGTG | Allows access to analog or binary BACnet lighting output objects.
|  | Structure | CMD_BLSG | Allows access to BACnet blind output objects.
Rule for defining BACnet Object ID
ObjID = ObjType * 2 ^ 22 + Instance
Rule for Objects created by IPA :
Instance > 10000
Instance to be unique within each ObjType